A9a.02									                      PACO PUMPS

1/06

NEW

# SUGGESTED SPECIFICATIONS

# Vertical Space Miser Split Coupled Pumps

# PC 132, Type VSMS

The contractor shall furnish and install, as shown in the drawings and as described in these specifications, PACO Type VSM Vertical Space Miser bronze fitted, single stage, centrifugal pump(s), as manufactured by PACO Pumps.

Each pump shall be capable of delivering _____ gallons per minute against a total head of _____ feet.  Pump(s) shall meet or exceed the efficiency shown in the pump schedule.

To insure stable operation, the pump curve shall be constantly rising from run-out to shut off.  To insure cavitation-free operation, each pump’s NPSH requirement must be low enough to permit stable, continuous operation at 120% or greater of best efficiency point.  Each pump shall be capable of continuous operation without producing noise in excess of Hydraulic Institute and OSHA guidelines.

Pump(s) shall (each) be coupled to a _____ HP, _____ RPM, _____ phase, _____ Hertz, _____ volt ball bearing drip-proof (special enclosure, specify: _____) Nema (standard, high efficiency) electric motor.  Motor shall be of such size that it will operate continuously without exceeding its HP rating, exclusive of service factor, at the design capacity and head.

Pump casing shall be ductile iron and shall be constructed with top pull-out capability.  Pumps shall have balanced double volute design to reduce radial thrust and to prolong seal and bearing life.  Pump casing shall incorporate a suction baffle to reduce pre-rotation and improve efficiency.  Suction and Discharge connections shall be the same size, flanged (125, 250) PSI rating, positioned in a manner to allow vertical piping without the need for elbows, guides, angle type valves, etc.  It shall be possible to move an "A Frame" hoist over the motor to facilitate motor removal without disturbing the piping.  Casing shall have bronze replaceable wear ring.  Impeller shall be cast bronze, enclosed, statistically, dynamically and hydraulically balanced, and shall be factory trimmed to match the delivery conditions indicated above.  Motor shaft shall be one piece steel with bronze shaft sleeve.  Pumps shall have internal mechanical seal suitable for the temperatures and pressures indicated, and shall be properly vented to the pump suction connection.  External seals shall not be acceptable.  The pump shall be coupled to the motor using a 2 piece axially split rigid coupling, located onto the shafts via annular rings.  Couplings relying on friction fit to tightening to maintain position on the shaft shall not be acceptable.  The coupling shall be so constructed to allow removal of the seal without removing or disturbing the motor.

The pump shall be mounted on a ductile iron stand with a minimum of 5 hold down holes, and support under the suction and discharge nozzle.  The entire unit shall not require grouting for operation within Hydraulic Institute Standards for Vibration.

All normally required spare and replacement parts shall be available in kit form and shall be field selectable from pump nameplate data.  It shall not be necessary to reference any drawing when selecting spare or replacement parts.